## Annexure-1
SR | TAG | DN | Type of valve | Valve GBS Location Building | Valve GBS Location Level | Valve GBS Location Room | Interfacing System | Type | Pressure Rating | Design Pressure Mpa (a) | Design Temp. °C | Nominal flow rate, kg/s | Quality Class | Seismic Class | Safety Class | HCC (Y/N)* | PED Category | Body Material | Material Composition Requirement [Co, Nb, Ta] | End Connection | Companion Flange Required | Flange Material | Sch1 In | Sch2 Out | Expected Full Open CV | Required Stroke Time (s) | Actuator Control | Actuator Control | Supply Air to Actuator for torque calculation [MPa-g] | Supply Air to Actuator for Design [MPa-g] | Fail Position | MAX Expected Valve + Actuator Weight [kg] | MAX Expected Height [mm] | MAX Expected Length [mm] | Expected Actuator Orientation (+90: Vertically up, 0: Horizontally) [°] | Radiation Aging - End of Life Radiation Dose at valve location [3FM52L_V1.1] [Gy] | Radiation Aging - Maximum Neutron flux at valve location [3FM52L_V1.1] [n.cm-2.s-1] | Radiation Aging - 1 MeV equivalent neutron fluence at valve location [3FM52L_V1.1] [n.cm-2] | Electro Magnetic Compatibility - Magnetic Field Modulus at valve location [85HR3P v4] with 1.4 safety factor [mT] | Acceleration Reference for Seismic Qualification [g] | Min Environment Temperature °C | Max Environment Temperature for nuclear operation °C | Max Environment Temperature for non-nuclear operation °C | Loss of HVAC Ambient Temperature °C | Fire Minimum Temperature | Upstream-Downstream Internal Leakage Standard & Class [EN 12266-1] | Internal Leak Tightness Direction | Stem and Bonnet External Leakage Standard & Class [ISO EN 15848-1] | Flange Leak Rate [EN13555] | Mechanical Cycle | Thermal Cycle | Loss of HVAC Cycle
1 | 26CCC1-VC-1023 | 200 | Pneumatic Butterfly Valve | 14 | L3 | 23 | TCWS_AUX_COOLING_HEADER | Modulating Control Valve | 300 | 1.72 | 190 | 74.1 | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 630 | 30-40 | Modulating | Psition Feedback | 0.6 | 1.1 | Fail to Close | 500 | 600 | 220 | 0 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 330 | C | Reverse | Ch | L0.01 | 10000 | 30000 | 50
2 | 26CCC1-VG-0292 | 200 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 300 | 1.72 | 190 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 630 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 500 | 600 | 220 | 45 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 330 | C | Reverse | Ch | L0.01 | 1000 | 30000 | 50
3 | 26CCC1-VG-1532 | 200 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 300 | 1.72 | 190 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 630 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 500 | 600 | 220 | 45 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 330 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
4 | 26CCC1-VG-0291 | 200 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 300 | 1.72 | 190 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 630 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 500 | 600 | 220 | 45 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 330 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
5 | 26CCC1-VG-0355 | 150 | Pneumatic Butterfly Valve | 14 | L3 | 23 | DY Compressors and HXs 14-L4 | On/Off | 300 | 1.72 | 100 | 49.2 | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 630 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 330 | 560 | 210 | 0 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | C | Reverse | Ch | L0.01 | 1000 | 30000 | 50
6 | 26CCC1-VG-0356 | 150 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 300 | 1.72 | 100 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 630 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 330 | 560 | 210 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
7 | 26CCC1-VG-1638 | 150 | Pneumatic Butterfly Valve | 14 | L3 | 23 | PBS31 and PBS32 | On/Off | 300 | 1.88 | 100 | 12.9 | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 630 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 330 | 560 | 210 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | D | Reverse | Ch | L0.01 | 1000 | 30000 | 50
8 | 26CCC1-VG-1637 | 150 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 300 | 1.88 | 100 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 630 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 330 | 560 | 210 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | D | Forward | Ch | L0.01 | 1000 | 30000 | 50
9 | 26CCC1-VC-1002 | 200 | Pneumatic Butterfly Valve | 14 | L3 | 23 | CVCS_IBED_HEAT_EX&SAMPLECOOLER | Modulating Control Valve | 600 | 5 | 100 | 57 | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 80S | 1100 | 30-40 | Modulating | Psition Feedback | 0.6 | 1.1 | Fail to Close | 620 | 900 | 230 | 0 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | C | Reverse | Ch | L0.01 | 10000 | 30000 | 50
10 | 26CCC1-VG-1562 | 200 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 100 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 80S | 80S | 1100 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 620 | 900 | 230 | 0 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | C | Reverse | Ch | L0.01 | 1000 | 30000 | 50
11 | 26CCC1-VG-1542 | 200 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 100 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 80S | 80S | 1100 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 620 | 900 | 230 | 0 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
12 | 26CCC1-VG-1561 | 200 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 100 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 80S | 40S | 1100 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 620 | 900 | 230 | 0 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
13 | 26CCC1-VC-1004 | 200 | Pneumatic Butterfly Valve | 14 | L3 | 23 | VVPHTS_ HEAT_EXCHANGER&V OLUME_CONTROL | Modulating Control Valve | 600 | 3.8 | 240 | 116 | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 80S | 1100 | 30-40 | Modulating | Psition Feedback | 0.6 | 1.1 | Fail to Close | 620 | 900 | 230 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 380 | C | Reverse | Ch | L0.01 | 10000 | 30000 | 50
14 | 26CCC1-VG-1609 | 200 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 3.8 | 240 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 80S | 80S | 1100 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 620 | 900 | 230 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 380 | C | Reverse | Ch | L0.01 | 1000 | 30000 | 50
15 | 26CCC1-VG-1544 | 200 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 3.8 | 240 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 80S | 80S | 1100 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 620 | 900 | 230 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 380 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
16 | 26CCC1-VG-1505 | 200 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 3.8 | 240 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 80S | 40S | 1100 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 620 | 900 | 230 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 380 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
17 | 26CCC1-VC-1005 | 200 | Pneumatic Butterfly Valve | 14 | L3 | 23 | TBM_PRIM_COOLING_SYS_OUTSIDE_PORT_CELL | Modulating Control Valve | 300 | 1.72 | 100 | 96 | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 1100 | 30-40 | Modulating | Psition Feedback | 0.6 | 1.1 | Fail to Close | 500 | 600 | 220 | 0 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | C | Reverse | Ch | L0.01 | 10000 | 30000 | 50
18 | 26CCC1-VG-1545 | 200 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 300 | 1.72 | 100 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 80S | 1100 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 500 | 600 | 220 | 0 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | C | Reverse | Ch | L0.01 | 1000 | 30000 | 50
19 | 26CCC1-VG-1568 | 200 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 300 | 1.72 | 100 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 80S | 40S | 1100 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 500 | 600 | 220 | 0 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
20 | 26CCC1-VG-1567 | 200 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 300 | 1.72 | 100 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 1100 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 500 | 600 | 220 | 0 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
21 | 26CCC1-VG-1085 | 250 | Pneumatic Butterfly Valve | 14 | L3 | 23 | CC1A HX | On/Off | 300 | 1.72 | 100 | 141.4 | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 2300 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 650 | 1100 | 250 | 0 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | D | Reverse | Ch | L0.01 | 1000 | 30000 | 50
22 | 26CCC1-VG-1087 | 250 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 300 | 1.72 | 100 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 2300 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 650 | 1100 | 250 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | D | Reverse | Ch | L0.01 | 1000 | 30000 | 50
23 | 26CCC1-VG-1102 | 250 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 300 | 1.72 | 100 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 2300 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 650 | 1100 | 250 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | D | Forward | Ch | L0.01 | 1000 | 30000 | 50
24 | 26CCC1-VG-1650 | 250 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 300 | 1.72 | 100 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 2300 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 650 | 1100 | 250 | 0 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | D | Forward | Ch | L0.01 | 1000 | 30000 | 50
25 | 26CC2A-VG-1084 | 250 | Pneumatic Butterfly Valve | 11 | L3 | 02W | 11-L3-02W | On/Off | 150 | 1.6 | 60 | 105.2 | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 2467 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 240 | 1220 | 165 | 45 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 200 | D | Reverse | Ch | L0.01 | 1000 | 30000 | 50
26 | 26CC2A-VG-1085 | 250 | Pneumatic Butterfly Valve | 11 | L3 | 02W |  | On/Off | 150 | 1.6 | 60 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 2467 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 240 | 1220 | 165 | 45 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 200 | D | Forward | Ch | L0.01 | 1000 | 30000 | 50
27 | 26CC2A-VG-0007 | 250 | Pneumatic Butterfly Valve | 11 | L3 | 02W |  | On/Off | 150 | 1.6 | 60 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 2467 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 240 | 1220 | 165 | 45 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 200 | D | Forward | Ch | L0.01 | 1000 | 30000 | 50
28 | 26CHH2-VG-0859 | 250 | Pneumatic Butterfly Valve | 14 | L4 | 22 | 14-L4-22 | On/Off | 150 | 1.34 | 45 | 132.31 | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 2467 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 240 | 1220 | 165 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 185 | D | Reverse | Ch | L0.01 | 1000 | 30000 | 50
29 | 26CHH2-VG-2024 | 250 | Pneumatic Butterfly Valve | 14 | L4 | 22 |  | On/Off | 150 | 1.34 | 45 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 2467 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 240 | 1220 | 165 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 185 | D | Forward | Ch | L0.01 | 1000 | 30000 | 50
30 | 26CHH2-VG-1830 | 250 | Pneumatic Butterfly Valve | 14 | L4 | 22 |  | On/Off | 150 | 1.34 | 45 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 2467 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 240 | 1220 | 165 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 185 | D | Forward | Ch | L0.01 | 1000 | 30000 | 50
31 | 26CCC1-VC-1022 | 300 | Pneumatic Butterfly Valve | 14 | L3 | 23 | IBED_PHTS_BAKING_HEAT_EXCH | Modulating Control Valve | 600 | 5 | 270 | 300 | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 80S | 2600 | 30-40 | Modulating | Psition Feedback | 0.6 | 1.1 | Fail to Close | 1000 | 1200 | 290 | 0 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 410 | C | Reverse | Ch | L0.01 | 10000 | 30000 | 50
32 | 26CCC1-VG-0293 | 300 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 270 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 80S | 80 | 2600 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 1000 | 1200 | 290 | 0 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 410 | C | Reverse | Ch | L0.01 | 1000 | 30000 | 50
33 | 26CCC1-VG-1531 | 300 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 270 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 80 | 80S | 2600 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 1000 | 1200 | 290 | 0 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 410 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
34 | 26CCC1-VG-0294 | 300 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 270 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 80S | 40S | 2600 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 1000 | 1200 | 290 | 0 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 410 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
35 | 26CHH2-VG-2025 | 300 | Pneumatic Butterfly Valve | 14 | L2 | TG2 | 14-L2-TG2 | On/Off | 150 | 1.34 | 45 | 256.61 | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 4024 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 430 | 1000 | 84 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 185 | D | Reverse | Ch | L0.01 | 1000 | 30000 | 50
36 | 26CHH2-VG-2183 | 300 | Pneumatic Butterfly Valve | 14 | L2 | TG2 |  | On/Off | 150 | 1.34 | 45 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 4024 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 430 | 1000 | 84 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 185 | D | Forward | Ch | L0.01 | 1000 | 30000 | 50
37 | 26CHH2-VG-1829 | 300 | Pneumatic Butterfly Valve | 14 | L2 | TG2 |  | On/Off | 150 | 1.34 | 45 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 40S | 4024 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 430 | 1000 | 84 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 185 | D | Forward | Ch | L0.01 | 1000 | 30000 | 50
38 | 26CCC1-VC-1006 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 | IBED_PHTS-B1_HEAT_EXCHANGER | Modulating Control Valve | 600 | 5 | 150 | 1202 | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 60 | 12800 | 30-40 | Modulating | Psition Feedback | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 290 | C | Reverse | Ch | L0.01 | 10000 | 30000 | 50
39 | 26CCC1-VG-0295 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 150 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 60 | 80 | 12800 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 290 | C | Reverse | Ch | L0.01 | 1000 | 30000 | 50
40 | 26CCC1-VG-1539 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 150 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 80 | 60 | 12800 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 290 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
41 | 26CCC1-VG-0296 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 150 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 60 | 40S | 12800 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 290 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
42 | 26CCC1-VC-1017 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 | IBED_PHTS-B2_HEAT_EXCHANGER | Modulating Control Valve | 600 | 5 | 150 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 60 | 12800 | 30-40 | Modulating | Psition Feedback | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 290 | C | Reverse | Ch | L0.01 | 10000 | 30000 | 50
43 | 26CCC1-VG-0297 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 150 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 60 | 80 | 12800 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 290 | C | Reverse | Ch | L0.01 | 1000 | 30000 | 50
44 | 26CCC1-VG-1537 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 150 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 80 | 60 | 12800 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 290 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
45 | 26CCC1-VG-0298 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 150 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 60 | 40S | 12800 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 290 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
46 | 26CCC1-VC-1018 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 | IBED_PHTS-B3_HEAT_EXCHANGER | Modulating Control Valve | 600 | 5 | 150 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 60 | 12800 | 30-40 | Modulating | Psition Feedback | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 290 | C | Reverse | Ch | L0.01 | 10000 | 30000 | 50
47 | 26CCC1-VG-0299 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 150 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 60 | 80 | 12800 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 290 | C | Reverse | Ch | L0.01 | 1000 | 30000 | 50
48 | 26CCC1-VG-1535 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 150 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 80 | 60 | 12800 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 290 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
49 | 26CCC1-VG-0300 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 150 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 60 | 40S | 12800 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 290 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
50 | 26CCC1-VC-1019 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 | IBED_PHTS-B4_HEAT_EXCHANGER | Modulating Control Valve | 600 | 5 | 150 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 60 | 12800 | 30-40 | Modulating | Psition Feedback | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 290 | C | Reverse | Ch | L0.01 | 10000 | 30000 | 50
51 | 26CCC1-VG-0301 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 150 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 60 | 80 | 12800 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 290 | C | Reverse | Ch | L0.01 | 1000 | 30000 | 50
52 | 26CCC1-VG-1533 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 150 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 80 | 60 | 12800 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 290 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
53 | 26CCC1-VG-0302 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 150 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 60 | 40S | 12800 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 290 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
54 | 26CCC1-VC-1003 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 | NBI-PHTS_HEAT_EXCHANGER | Modulating Control Valve | 600 | 5 | 100 | 900 | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 40S | 60 | 12800 | 30-40 | Modulating | Psition Feedback | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | C | Reverse | Ch | L0.01 | 10000 | 30000 | 50
55 | 26CCC1-VG-1559 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 100 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 60 | 80 | 12800 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | C | Reverse | Ch | L0.01 | 1000 | 30000 | 50
56 | 26CCC1-VG-1652 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 100 |  | QC-1 | SC-1(SF) | SIC-2 | YES | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 80 | 60 | 12800 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
57 | 26CCC1-VG-1560 | 600 | Pneumatic Butterfly Valve | 14 | L3 | 23 |  | On/Off | 600 | 5 | 100 |  | QC-1 | SC-1(SF) | SIC-2 | NO | TBD | ASTM A351 Gr CF8M | Co≤0.2%; Nb≤0.1%; Ta≤0.05% | Lug Type,FL | Yes | A182 F304L | 60 | 40S | 12800 | 30-40 | On/Off | Limit Switches | 0.6 | 1.1 | Fail to Close | 3500 | 2000 | 390 | 90 | 10 | 100 | 100000000 | 21 | 4 | 5 | 35 | 40 | 80 | 240 | C | Forward | Ch | L0.01 | 1000 | 30000 | 50
*HCC-N :-The valve is installed on a HCC line but is not required to operate during or after a SL3 event.